Progress Report No 6

LIFE00/ ENV/EE/000924

Estwaste




Annex 2


Results of wastewater analysis collected from pre-treatment sections of Kambja and Kadrina prototypes

Prototype
Parameter
No of samples
Before pretreatment
After 1st stage of pretreatment
After 2nd stage of pretreatment

Kambja
BOD7(mgO/l)
13
60,5
24,0
21,3

Kambja
total N (mg/l)
13
21,4
18,0
15,5

Kambja
total P (mg/l)
13
3,0
2,8
2,9

Vohnja
BOD7(mgO/l)
11
1321,8
37,7
20,9

Vohnja
total N (mg/l)
11
133,6
25,9
14,1

Vohnja
total P (mg/l)
11
20,1
5,2
1,1

Kihlevere
BOD7(mgO/l)
13
188,0
215,9
21,4

Kihlevere
total N (mg/l)
13
69,5
72,1
45,2

Kihlevere
total P (mg/l)
13
9,9
15,3
3,8

